APPENDIX I

Water meter sizing worksheet

Dallas Water Utilities

| Water Meter Sizing Worksheet Dallas Water Utilities |
| --- |
| Project Information |
| Project Name |  |
| Project Address |  |
| Project Lot & Square |  |
| Owner’s Name |  |
| Owner’s Address |  |
| Owner’s Phone or Email |  |
| Designer Information |
| Designer’s Name |  |
| Designer’s Company |  |
| Designer’s Address |  |
| Designer’s Phone and/or Email |  |
| Type of Occupancy |
| Residential: Single Family Home Duplex Townhouse Clustered Housing Multifamily Mobile Home Others: Non Residential: Office Retail Commercial/Industrial Central Area Mixed Use Multiple Commercial Urban Corridor Others: |
| Hydrant Flow Test Results |
| Static Pressure (psi): Residual Pressure (psi): Gage Pressure (psi): |
| A hydrant flow test is required for a water connection 3" diameter and larger. Case 1: If your connection is 2" and smaller, assume a working pressure at meter discharge of 60 psi and a pressure adjustment factor of 1.0. Case 2: If your connection is larger than 2”, use pressure adjustment factor from Table 3. |
| Signature |
| The designer is responsible for determining required domestic, irrigation, mechanical, and fire flows in addition to the proper sizing of meters. By submitting this application, I affirm that the information provided is correct. |
| Designer’s Name (printed) |  |
| Signature/Date |  |

Table 1:  Water Demand Calculation

| Domestic Demand (Continuous) |
| --- |
| Fixture Type (Standardized at 60 psi) | Fixture value (gpm) |  | Number of Fixtures |  | Total Fixture Value (gpm) |
| Bathtub | 8 | x |  | = |  |
| Bedpan Washers | 10 | x |  | = |  |
| Bidet | 2 | x |  | = |  |
| Dental Unit | 2 | x |  | = |  |
| Drinking Fountain (public) | 2 | x |  | = |  |
| Faucet (kitchen sink) | 2.2 | x |  | = |  |
| Faucet (lavatory) | 1.5 | x |  | = |  |
| Shower Head (shower only) | 2.5 | x |  | = |  |
| Faucet (utility sink) | 4 | x |  | = |  |
| Urinal (flush valve) | 35 | x |  | = |  |
| Urinal (wall or stall) | 16 | x |  | = |  |
| Urinal Trough (2 ft. unit) | 2 | x |  | = |  |
| Toilet Flush Valve | 35 | x |  | = |  |
| Toilet Tank Type | 4 | x |  | = |  |
| Dishwasher | 2 | x |  | = |  |
| Clothes Washer | 6 | x |  | = |  |
| Hose (50 ft length wash down) 1/2" connection | 5 | x |  | = |  |
| Hose (50 ft length wash down) 5/8" connection | 9 | x |  | = |  |
| Hose (50 ft length wash down) 3/4" connection | 12 | x |  | = |  |
| other |  | x |  | = |  |
| Total Fixture Value | = |  |
| Water Flow Demand Per Fixture Value (Figures 1 & 2), gpm | = |  |
| Pressure Adjustment Factor (Table 3) | = |  |
| Water Flow Demand x Pressure Factor, gpm | = |  |
| Total Domestic Demand, gpm | = |  |

Table 1:  Water Demand Calculation

Contd.

| Irrigation Demand (Intermittent) |
| --- |
|  | 100 Sq. Ft. |  | Factor |  | Fixture Value (gpm) |
| Irrigated Area with Spray Systems |  | x | 1.16 | = |  |
| Irrigated Area with Rotary Systems |  | x | 0.40 | = |  |
| Number of Hose Bibs (1/2") |  | x | 5.0 | = |  |
| Number of Hose Bibs (5/8") |  | x | 9.0 | = |  |
| Number of Hose Bibs (3/4") |  | x | 12.0 | = |  |
| Sub-Total Irrigation Demand (Irrigation + Hose Bib), gpm | = |  |
| Pressure adjustment factor (Table 3) | = |  |
| Sub-Total Irrigation Demand x Pressure Factor, gpm | = |  |
| Total Fixed Demands (if any), gpm | = |  |
| Total Irrigation Demand, gpm | = |  |
| Mechanical Demand (Continuous and/or Intermittent) |
| Total Continuous Mechanical Demand** gpm | = |  |
| Total Intermittent Mechanical Demand** gpm | = |  |
| *Mechanical water demand refers to the intermittent and/or continuous operation of process equipment, cooling towers, A/C systems, wash down systems, etc. It is the responsibility of the MEP to determine those demand values based on type of equipment and usage. |
| Fire Demand, if required by code (Intermittent) |
| Does the building require a fire pump? |  | Yes |  | No |
| Actual Fire Flow Demand (Per NFPA Requirements) gpm | = |  |
| Pump Test Demand (if required, 150% of actual demand) gpm | = |  |

Table 2:  Water Service Allocation and Meter Selection

| Service Type | * Lateral Size (in) | Meter Size (in) | **Meter Type |
| --- | --- | --- | --- |
| Small Domestic (5/8”- 2”) Optional Irrigation |  |  |  |
| Large Domestic (> 2”) |  |  |  |
| Optional Irrigation Bypass |  |  |  |
| Dedicated Fire Service (4”- 10”) Detector Check Device Bypass |  |  |  |
| Dedicated Irrigation Service (2”- 10”) |  |  |  |
| Small Combined Water and Fire (1”- 2”) Domestic Water Lateral Fire Line (Internal Sprinkler) |  |  |  |
| Large Combined Water and Fire (4”- 10”) Domestic Water Lateral (Max. 2”) Fire Line (Internal Sprinkler) Strainer Bypass |  |  |  |

Reference: See §2.12.5(Water Meter) of Water and Wastewater Procedure and Pipeline Design manual for

additional requirements on water service and meters

Note:  * The velocity in the lateral must be ≤ 15 fps.

**  See Table 2 for recommended meter type as applicable.

Table 3: Pressure adjustment factors (60 psi)

| Working Pressure at Meter Discharge (psi) | Pressure Adjustment Factor |
| --- | --- |
| 35 | 0.74 |
| 40 | 0.80 |
| 50 | 0.90 |
| 60 | 1.00 |
| 70 | 1.09 |
| 80 | 1.17 |
| 90 | 1.25 |
| 100 | 1.34 |

Source:  AWWA M22: Sizing Water Service Lines and Meters, Second Edition

Note:

Working pressure at meter discharge = Static pressure in the main. Information is

obtained from a fire hydrant flow test.

A hydrant flow test is required for a water connection 3" diameter and larger. If your

connection is 2" and smaller assume a working pressure at meter discharge of 60 psi

and a pressure adjustment factor of 1.0.

| Meter Type (inch) | Min. Flow Rate (gpm) | Low Normal Flow Rate (gpm) | Change Over Range | High Normal Flow Rate (gpm) | Max. Flow Rate (gpm) | Headloss at Max. Flow (psi) |
| --- | --- | --- | --- | --- | --- | --- |
| Positive Displacement |
| 5/8 ¾ 1 1½ 2 | 0.25 0.50 0.75 1.5 2 | 1 2 3 5 8 | N/A | 10 15 25 50 80 | 20 30 50 100 160 | 15 15 15 15 15 |
| Turbine Class I: Vertical Shaft, Low Velocity |
| 1 1½ 2 3 4 6 | 2 3 4 6 8 15 | N/A | N/A | 35 65 100 220 420 865 | 50 100 160 350 630 1,300 | 15 15 15 15 15 15 |
| Turbine Class II: Horizontal Axis, High Velocity, In-line |
| 1½ 2 3 4 6 8 10 | 4 4 8 15 30 50 75 | N/A | N/A | 80 100 240 420 920 1,600 2,500 | 120 160 350 630 1,400 2,400 3,800 | 7 7 7 7 7 7 7 |

Table 4:  Recommended Meter Type

Table 4:  Recommended Meter Type

Contd.

| Meter Type (inch) | Min. Flow Rate (gpm) | Low Normal Flow Rate (gpm) | Change Over Range | High Normal Flow Rate (gpm) | Maximum Flow Rate (gpm) | Headloss at Max. Flow (psi) |
| --- | --- | --- | --- | --- | --- | --- |
| Multi Jet |
| 1 1½ 2 | 0.75 1.5 2.0 | 3 5 8 | N/A | 25 50 80 | 50 100 160 | 15 15 15 |
| Compound |
| 2 3 4 6 | 0.25 0.5 0.75 1.5 | 2 4 6 10 | 20 23 28 32 | 80 160 250 500 | 160 320 500 1,000 | 20 20 20 20 |
| Factory Mutual (FM) |
| 4 6 8 10 |  | 2 4 7 12 | 1 1 ½ 2 2 | 700 1600 2800 4400 | 1500 3100 8000 8000 | 12 19 14 12 |
| Detector Check (DC) |
| 4 6 8 10 | 0.25 0.25 0.25 0.25 |  |  |  | 750 850 2000 5000 |  |

Figure 1: Water Flow Demand per Fixture Value – Low Range

Source:  AWWA M22: Sizing Water Service Lines and Meters, Second Edition

Figure 2: Water Flow Demand per Fixture Value – High Range

Source:  AWWA M22: Sizing Water Service Lines and Meters, Second Edition

# Text boxes

I

I

H

H

I

I

I

I

I

I

I